## Sheet1
acquired	name	type	unit	divisor	header	command	label	description
x	t_hs	float	deg	10	190	3100FA01D60000	T-HS	The current temperature (TVBH) of the heat generator is displayed in C.
x	t_hs_set	float	deg	10	190	31000200000000	T-HS Setpoint	The current Inflow target temperature of the heat generator is displayed in C
x	water_pressure	float	bar	1000	190	31001C00000000	Water Pressure	The current water pressure is displayed in bar.
x	t_ext	float	deg	10	310	6100FA0A0C0000	T-Outside	The average external temperature is displayed C.
x	t_dhw	float	deg	10	190	31000E00000000	T-DHW	The current temperature of the hot water storage tank is displayed in C. If there is no hot water function activated, --- is displayed.
x	t_dhw_set	float	deg	10	190	31000300000000	T-DHW Setpoint	The current target hot water temperature is displayed in C. If there is no hot water function activated, --- is displayed. The current set value is here always the maximum value of all relevant demands for this hot water circuit
x	t_return	float	deg	10	190	31001600000000	T-Return	The current return flow temperature of the heat generator is displayed in C. If there is no relevant sensor connected to the heat generator, --- is displayed.
x	flow_rate	longint	lh	1	190	3100FA01DA0000	Flow Rate	The filtered value of the current volume flow in litres per hour
x	t_hc	float	deg	10	610	C1000F00000000	T-HC	The inflow temperature in the direct heating circuit is displayed in C.
x	t_hc_set	float	deg	10	310	61000400000000	T-HC Setpoint	The set temperature of the flow in the direct heating circuit is displayed in C.
x	status_pump	value		1	190	3100FA0A8C0000	Status HS Pump	The current status of the internal heat circulation pump in the ROTEX HPSU compact is displayed.
x	runtime_comp	longint	hour	1	190	3100FA06A50000	Runtime Compressor	The running time of the refrigerant compressor is displayed in h.
x	runtime_pump	longint		1	190	3100FA06A40000	Runtime Pump	The running time of the internal heating circulation pump is displayed in h.
x	posmix	longint	percent	1	190	3100FA069B0000	Mixer Position	The current position of the 3UV DHW 3-way switch valve is displayed. 0%: position A (room heating) 100%: position B (domestic hot water generation)
x	qboh	longint	kwh	1	190	3100FA091C0000	Qboh	The amount of heat in the additional heat generator for hot water generation is displayed in kWh.
	qchhp	longint	kwh	1	190	3100FA09200000	Qchhp	The amount of heat in the additional heat generator for heating mode is displayed in kWh.
	qsc	longint	kwh	1	190	3100FA06A60000	Qsc	The quantity of heat in the heat pump for cooling is displayed in kWh.
x	qch	longint		1	190	3100FA06A70000	Qch	The quantity of heat in the heat pump for heating is displayed in kWh.
x	qwp	longint	kwh	1	190	3100FA09300000	QWP	The total amount of heat in the heat pump is displayed in kWh.
x	qdhw	longint	kwh	1	190	3100FA092C0000	Qdhw	The quantity of heat for hot water generation is displayed in kWh.
	sw_vers_01	longint		1	190	3100FA01990000	Version SW 1	Version SW 1
	sw_vers_02	longint		1	190	3100FAC0B40000	Version SW 2	Version SW 2
	sw_vers_03	longint		1	190	3100FA024B0000	Version SW 3	Version SW 3
	mode_01	int		1	190	3100FA01120000	Modo ?	Modo Rotex
x	tvbh2	float	deg	10	190	3100FAC102	TVBH2 [C]	Current heating inflow temperature or temp. after heating support heat exchanger (tV,BH).
x	tliq2	float	deg	10	190	3100FAC103	Tliq2 [C]	Current coolant temperature (tliq2).
	tr2	float	deg	10	190	3100FAC104	TR2 [C]	Current heating return flow temperature, secondary sensor (tR2).
	ta2	float	deg	10	190	3100FAC105	TA2 [C]	Actual outdoor temperature (measured by temperature sensor of the external heat pump)
	tdhw2	float	deg	10	190	3100FAC106	Tdhw2 [C]	Current temperature in domestic hot water storage tank, secondary sensor (tDHW2).
	quiet	value	longint	1	190	3100FAC107	quiet	Shows the status of the whisper mode.
x	mode	longint	longint	1	190	3100FAC0F6	Mode	Current mode of the heat pump: ---: No heating or cooling demand : Heating : Cooling : Domestic hot water generation : Automatic defrosting function active
x	pump	longint	percent	1	190	3100FAC0F7	Pump	Actual output of the internal heating circulation pump in %
	ext	longint	longint	1	190	3100FAC0F8	Ext	Current energy mode of the heat pump: LT: EVU function HT/NT active and low tariff. HT: EVU function HT/NT active and high tariff. SGN: EVU function SMART GRID active, normal mode. SG1: EVU function SMART GRID active, disconnection: no heat pump operation, no frost protection function. SG2: EVU function SMART GRID active, switchon recommendation, mode with higher set temperatures, cheap power. SG3: EVU function SMART GRID active, switchon command and storage tank charging to 70 C, cheap power - - -: No external mode active, heat pump works in normal mode.
x	ehs	longint	kwh	1	190	3100FAC0F9	EHS	Current output of the backup heater in kW
	rt	longint	longint	1	190	3100FAC0FA	RT	Parameter [Room thermostat] / [Interlink fct]
x	bpv	longint	percent	1	190	3100FAC0FB	BPV	Current position of the mixing valve 3UVB1 (100% = A, 0% = B)
	t_v1	float	deg	10	190	3100FAC0FC	TV	Current inflow temperature after the plate heat exchanger (tV1)
	t_dhw1	float	deg	10	190	3100FAC0FD	Tdhw	Current temperature in domestic hot water storage tank (tDHW1)
x	t_vbh	float	deg	10	190	3100FAC0FE	TVBH	Current heating inflow temperature or temp. after heating support heat exchanger (tV,BH)
	t_outdoor_ot1	float	deg	10	190	3100FAC0FF	TA	Actual outdoor temperature (measured by optional temperature sensor RoCon OT1)
	t_r1	float	deg	10	190	3100FAC100	TR	Current heating return flow temperature (tR1)
x	v1	longint	lh	1	190	3100FAC101	V	Actual volume flow (flow rate) in the heating system
	t_room1_setpoint	float	deg	10	190	31000500000000	T Room 1 Setpoint	Setpoint 1 value
	t_room2_setpoint	float	deg	10	190	31000600000000	T Room 2 Setpoint	Setpoint 1 value
	t_room3_setpoint	float	deg	10	190	31000700000000	T Room 3 Setpoint	Setpoint 1 value
	heat_slope	float		100	190	3100FA010E0000	Heat-Slope	Heat Slope
	t_dhw_setpoint1	float	deg	10	190	31001300000000	T-ACS nom 1	Nominal value of the hot water temperature in C, which is valid for the first ignition cycle
	t_dhw_setpoint2	float	deg	10	190	3100FA0A060000	T-ACS nom 2	Nominal value of the hot water temperature in C, which is valid for the second ignition cycle
	t_dhw_setpoint3	float	deg	10	190	3100FA013E0000	T-ACS nom 3	Nominal value of the hot water temperature in C, which is valid for the third ignition cycle
	hyst_hp	float	deg	10	190	3100FA06910000	Hyst HP	Switching threshold hot water charging. Setting of the temperature difference to which the temperature in the domestic hot water storage tank compared to the current target hot water temperature [T-DHW Setpoint] can drop before the heat pump is switched on to provide hot water
	t_flow_cooling	float	deg	10	190	3100FA03DD0000	T-Flow Cooling	Setting the cooling inflow target temperature (fixed value) when cooling mode is active
	error	value		1	190	3100FA13880000	error	errorcode
	outdoor_type	value	KW	1	190	3100FA069A0000	Outdoor type	Type exterior heat pump unit
	indoor_unit	value	longint	1	190	3100FA06990000	Indoor unit	Type of interior heat pump unit
	func_heating	value	int	1	190	A100FA06D20000	Function Heating	Setting as to whether there is an additional heat generator (WEZ) for hot water generation and heating support
	hzu	value	longint	1	190	3100FA066C0000	HUZ	Heating support from domestic hot water storage tanks when the minimum temperature is exceeded
	equi_func	value	longint	1	190	A100FA06D30000	Equilibrium Function	The bivalence function is relevant for operation of the optional ancillary heater based on a backup demand (room heating operation)
	smart_grid	value	longint	1	190	3100FA06930000	SMART GRID	Smart Grid
	modus_sg	value	longint	1	190	3100FA06940000	Mode SG	Only if parameter [SMART GRID] = 1:Used for a possible target temperature increase in the case of aSMART GRID start command
	ht_nt_func	value	longint	1	190	3100FA066F0000	HT/NT Function	Setting which specifies which heat sources are switched off when the standard signal is received from the energy supply company (EVU) in the case of the customer having an off-peak tariff network connection
	ht_nt_contact	value	longint	1	190	3100FA06700000	HT/NT Contact	Specifies whether the HT/NT input is an NC or NO contact
	room_therm	value	longint	1	190	3100FA06780000	Room thermostat	Configuration of a room thermostat connected to the port J16 on the ROTEX HPSU compact using potential-free contacts
	interlink	value	longint	1	190	3100FA06790000	Interlink fct	Configuration for systems operating with 2 different inflow target temperatures
	air_purge	value	longint	1	190	3100FA06950000	Air Purge	Activation of automatic bleeding of the ROTEX HPSU compact and the connected heating circuit
	max_perf_pump	longint	percent	1	190	3100FA067E0000	Max Perform Pump	Upper limit for modulation of the pump output
	min_perf_pump	longint	percent	1	190	3100FA067F0000	Min Perform Pump	Lower limit for modulation of the pump output
	outside_conf	value	sval	1	190	3100FA09610000	Outside Config	Configuration of the optional external temperature sensor RoCon OT1
	storage_conf	value	sval	1	190	3100FA09610000	Storage Config	Configuration of water heating
	pres_conf	value	sval	1	190	3100FA09610000	Pressure Config	Configuring the sensor for assessment of the system water pressure
	out_temp_adapt	float	deg	10	190	6100FA0C1F0000	Outside Temp Adap	Individual adapting for the measured value of the outdoor temperature relevant for the Controller
	power_dhw	longint	w	0.1	190	3100FA06680000	Power DHW	Heating output of electric auxiliary heater for hot water generation
	buh_s1_pow	longint	w	0.1	190	3100FA06690000	BUH s1 power	Heat capacity of the ancillary electric heater in Stage 1 heating support
	buh_s2_pow	longint	w	0.1	190	3100FA066A0000	BUH s2 power	Heat capacity of the ancillary electric heater in Stage 2 heating support
	power_biv	longint	w	0.1	190	3100FA066B0000	Power BIV	Setting limits the output of the heating support
	tdiff_dhw_ch	longint		10	190	3100FA066D0000	TDiff-DHW CH	TDiff-DHW CH
	t_vbh1_max	float	deg	10	190	3100FA066E0000	T vbh1 max	Setting limits the inflow temperature (measured at tV, BH) with active heating support function
	equi_temp	float	deg	10	190	A100FA06D40000	Equilibrium Temp	Setting affects the operation of the potential-free AUX switching contact (toggle switch utput A) defined in the parameter [AUX Fct]
	quiet_mode	value	longint	1	190	3100FA06960000	Quiet Mode	Mode for low-noise operation with reduced output
	aux_fct	value	longint	1	190	3100FA06710000	AUX Fct	Setting assigns the switching conditions to the potential-free AUX contact (toggle switch output A)
	aux_time	longint	sec	1	190	3100FA06720000	AUX time	AUX switching contact (A) switches with a delay when the switching condition is pending for longer than the set time
	t_dhw_1_min	float	deg	10	190	3100FA06730000	T-DHW 1 min	Switching threshold storage tank temperature (Tdhw) for AUX switching contact (see parameter [AUX Fct])
	delta_t_ch	float	deg	10	190	3100FA06830000	Delta-T CH	Set outdoor temperature spread The ROTEX HPSU compact heating circulation pump controls the flow rate in order to achieve the set spread between the inflow target temperature and the return flow temperature (tV, BH â tR1)
	v_var	longint	lh	10	190	3100FA069C0000	V var	Current minimum necessary volume flow in the system (calculated value, not configurable)
	t_flow_ch_adj	float	deg	10	190	3100FA06A00000	T-Flow CH adj	Only when parameter [Interlink fct] = On. With a closed cooling RT switching contact, the inflow target temperature is increased by the set value
	t_flow_cool_adj	float	deg	10	190	3100FA06A10000	T-Flow Cooling adj	Only when parameter [Interlink fct] = On. With a closed cooling RT switching contact, the cooling inflow target temperature is reduced by the set value
	min_pressure	float	bar	1000	190	3100FA07280000	Min Pressure	Defines the minimum water pressure
	max_pressure	float	bar	1000	190	3100FA07270000	Max Pressure	Defines the maximum water pressure
	setpoint_pressure	float	bar	1000	190	3100FA07250000	Set Point Pressure	Defines the set water pressure
	max_pressure_drop	float	bar	1000	190	3100FA07260000	Max Pressuredrop	Defines the maximum acceptable pressure drop in the heating system
	hc_func	value	longint	1	190	6100FA01410000	HC Function	Setting defines the type of inflow temperature control
	t_frost_protect	longint	deg	1	190	6100FA0A000000	T-Frost Protect	0=No frost protection of the heating circuit, Otherwise: If the outside temperature falls below the programmed value, the system switches into the frost protection mode (switches the pumps on). The function ceases once the outside temperature has risen to the set value +1 K
	insulation	value	longint	1	190	6100FA010C0000	Insulation	Setting the insulation standard of the building. This affects the way the heating curve and the heating times automatically adapt to the outside temperature.
	screed	value	longint	1	190	6100FA011A0000	Screed	Function for screed drying
	screed_day1	float	deg	10	190	6100FA0BB90000	Temp screed day 1	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day2	float	deg	10	190	6100FA0BBA0000	Temp screed day 2	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day3	float	deg	10	190	6100FA0BBB0000	Temp screed day 3	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day4	float	deg	10	190	6100FA0BBC0000	Temp screed day 4	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day5	float	deg	10	190	6100FA0BBD0000	Temp screed day 5	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day6	float	deg	10	190	6100FA0BBE0000	Temp screed day 6	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day7	float	deg	10	190	6100FA0BBF0000	Temp screed day 7	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day8	float	deg	10	190	6100FA0BC00000	Temp screed day 8	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day9	float	deg	10	190	6100FA0BC10000	Temp screed day 9	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day10	float	deg	10	190	6100FA0BC20000	Temp screed day 10	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day11	float	deg	10	190	6100FA0BC30000	Temp screed day 11	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day12	float	deg	10	190	6100FA0BC40000	Temp screed day 12	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day13	float	deg	10	190	6100FA0BC50000	Temp screed day 13	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day14	float	deg	10	190	6100FA0BC60000	Temp screed day 14	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day15	float	deg	10	190	6100FA0BC70000	Temp screed day 15	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day16	float	deg	10	190	6100FA0BC80000	Temp screed day 16	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day17	float	deg	10	190	6100FA0BC90000	Temp screed day 17	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day18	float	deg	10	190	6100FA0BCA0000	Temp screed day 18	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day19	float	deg	10	190	6100FA0BCB0000	Temp screed day 19	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day20	float	deg	10	190	6100FA0BCC0000	Temp screed day 20	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day21	float	deg	10	190	6100FA0BCD0000	Temp screed day 21	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day22	float	deg	10	190	6100FA0BCE0000	Temp screed day 22	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day23	float	deg	10	190	6100FA0BCF0000	Temp screed day 23	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day24	float	deg	10	190	6100FA0BD00000	Temp screed day 24	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day25	float	deg	10	190	6100FA0BD10000	Temp screed day 25	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day26	float	deg	10	190	6100FA0BD20000	Temp screed day 26	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day27	float	deg	10	190	6100FA0BD30000	Temp screed day 27	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	screed_day28	float	deg	10	190	6100FA0BD40000	Temp screed day 28	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	t_out_lim_day	float	deg	10	190	6100FA01160000	T-Outside lim day	Setting the procedural program for screed heating. An individual inflow temperature can be set for each day for a maximum period of 28 days. The end of the screed programme is defined by the 1st. Day at target value setting
	t_out_lim_night	float	deg	10	190	6100FA01170000	T-Outside lim night	Parameter for setting the heating limit for "Switch-off" of the heating circuit during economy mode
	t_flow_day	float	deg	10	190	6100FA01290000	T-Flow Day	Setting the inflow target temperature for the heating circuit during the heating time when in operating mode: "Automatic 1", "Automatic 2", "Heating"
	t_flow_night	float	deg	10	190	6100FA012A0000	T-Flow night	Setting the inflow target temperature for the heating circuit during the setback time when in operating mode: "Automatic 1", "Automatic 2", "Reducing"
	max_t_flow	float	deg	10	190	61002800000000	Max T-Flow	The inflow temperature determined for the heating circuit is limited to the maximum value set here
	min_t_flow	float	deg	10	190	6100FA012B0000	Min T-Flow	The inflow temperature determined for the heating circuit is limited to the minimum value set here
	hc_adapt	value	longint	1	190	6100FA01150000	HC Adaption	HC Adapation
	start_tout_cool	float	deg	10	190	6100FA135B0000	Start T-Out Cooling	Setting from which outside temperature the cooling operation with the highest cooling infeed target temperature
	max_tout_cool	float	deg	10	190	6100FA135C0000	Max T-Out Cooling	Setting to determine from which outdoor temperature the lowest cooling flow temperature
	t_flow_cool_start	float	deg	10	190	6100FA135D0000	T-Flow Cooling start	Setting the cooling inflow target temperature at the start of cooling mode
	t_flow_cool_max	float	deg	10	190	6100FA135E0000	T-Flow Cooling max	Setting the minimum cooling inflow target temperature. This is kept constant relative to the outside temperature
	min_t_flow_cool	float	deg	10	190	6100FA13630000	Min T-Flow Cooling	Setting the absolute lower limit of the cooling inflow target temperature. The limitation is effective if a lower cooling inflow target temperature is determined based on other parameter settings
	t_flow_cool	float	deg	10	190	6100FA03DD0000	T-Flow Cooling	Setting the cooling inflow target temperature (fixed value) when cooling mode is active
	cool_setpoint_adj	float	deg	10	190	6100FA13590000	Cooling Setpoint adj	Parallel displacement of the cooling characteristic curve to match the set value
	circ_pump_dhw	value	longint	1	190	3100FA01820000	Circl-Pump DHW	Setting for activating a circulation pump
	circ_pump_interval	value	longint	1	190	3100FA065E0000	Circl-Pump Interval	Setting the interval control for an optional circulation pump
	anti_leg_day	value	longint	1	190	3100FA01010000	Anti-Legionella day	Setting the day for the thermal disinfection of the circulating tank
	anti_leg_time	value	longint	1	190	3100FAFDF40000	Anti-Legionella time	Setting the start time of the thermal disinfection of the hot water circulating tank
	anti_leg_temp	float	deg	10	190	3100FA05870000	Anti-Legionella temp	Setting the hot water target temperature during thermal disinfection of the hot water circulating tank
	max_dhw_loading	longint	min	1	190	3100FA01800000	Max DHW loading	Setting limits the time period for hot water generation to the set target value
	dhw_off_time	float		1	190	3100FA4E3F0000	DHW Off Time	Setting the block time following completion or interruption of a hot water generation cycle. New demand of hot water generation is satisfied only after expiry of this block time
	one_hot_water	value	longint	1	190	3100FA01440000	1x Hot Water	Start of the one-off heating up of the hot water and the set value [T-DHW Setpoint 1], independent of the heating programmes
	timer_boh	longint	min	1	190	3100FA06920000	Timer BOH	Delay time after which the reserve heating may support the heat pump in hot water charging
	t_reduced	float	deg	10	190	61000800000000	T-Reduced	Target room temperature for the setback times for the permanent timer programmes [Automatic 1] and [Automatic 2]
	t_absence	float	deg	10	190	6100FA013D0000	T-Absence	Target room temperature for the setback times for the temporary timer programmes [Away] and [Vacation]
	t_room	float	deg	10	190	8100FA00110000	T-Room	Room temperature measured by an optional Rocon U1 room station